## Slide 1: SIAAP Resources recovery policy
Notes: In the context of a growing population around the World, with Climate change risks and resources scarcity, each one has contribute to recover materials and to a carbon neutral society. This one of the duties of sewage treatment as well as solid waste utilities.
SIAAP is now strongly committed in these challenges of resources recovery and green energy production
My presentation aims at show the works that are currently in progress at SIAAP

## Slide 2: SUMMARY
Biogas: resources recovery
Sludge: resources recovery
    - Foccus on agricultural valorization
- Foccus on energy recovery
Biogas: resources recovery prospects
Sludge: resources recovery prospects

## Slide 3: Waste water as a resource
245 g TSS
180 g BOD5
430 g COD
50 g N
5 g P
1.1 kWh
1 m3 Water is:
Energy
For the treatment of 1 m3 = 1.25 kWh
Biogas:
0.7 kWh
Sludge:
0.4 kWh
Notes: Sewage treatment spend lots of energy but it’s also a resource that we have to use if we don’t want to spend too much money

## Slide 4: BIOGAS Resources recovery

## Slide 5
Source SIAAP
19 000 tDM
6 600 tDM
1 100 tDM
Sludge b.t : 231 700 tDM
Total SIAAP 2017 :
133 700 tDM
55 100 tDM
16 200 tDM
Sludge production before treatment
Notes: Chiffres arrondis
Pour mémoire : 233 200 tMS extraites de la file eau

## Slide 6
Source SIAAP
14 MNm3
60 MNm3
16MNm3
Digestion
19 000 tDM
6 600 tDM
1 100 tDM
Biogas prod. : 91 MNm3
Total SIAAP 2017 :
Sludge treatment
133 700 tDM
55 100 tDM
16 200 tDM
Biogas production
Sludge b.t : 231 700 tDM
Notes: Sludge was just considered for a long time as waste : the main objective of sludge treatment was to dry, to reduce the volume evacuated
but, it can also produce energy
in SIAAP, 3 Wastewater Treatment Plant includes digestion in their treatment, first of all to reduce the sludge volume. But, it produce also energy which can be used for the plant.
Today, we consume almost all of our biogas production to power our energy processes

## Slide 7: SIAAP energy balance
Biogas: 552 GWh  48% needs covered
Electricity: 522 GWh
  Electric selfproduction: 36 GWh (7%)
  Sewage network (pumping): 45 GWh (8%)
Fuel: 17 GWh
Natural gas: 61 GWh
 Average consumption: 1.32 kWh/m3 or 6.24 kWh/kg BOD5 removed
WWTP and sewage network energy balance
Notes: 520 (five hundred and twenty) GWh PCS consumed : TAG (gas turbines), digestion, sludge conditioning
Nowadays, the production of biogas or sludge incineration is not important enough to be self-sufficient. That’s why we continue to consider sludge as a ressource under exploited, and why we study another ways to increase energy production with sludge

## Slide 8: SLUDGE Resources recovery

## Slide 9
Source SIAAP
Digestion
Drying
Thermal conditioning
Incineration
54 100 tDM
18 100 tDM
12 300 tDM
30 500 tDM
6 200 tDM
1 400 tDM
Sludge treatment
Sludge production after treatment
Biogas prod. : 91 MNm3
Total SIAAP 2017 :
Sludge a.t. : 122 600 tDM
Sludge b.t : 231 700 tDM
Notes: From one wastewater treatment plant to another, we have different modes of treatment.
These different treatments will produce sludge of different characteristics

## Slide 10: Seine aval sludge spreading
The different types of sludge:
    Dried sludge: dryness of 85 to 95%
      Ressources recovery: Cement plant - Composting
    Sludge dehydrated by filter press: dryness of +/- 50%
      Ressources recovery: Land application - Composting
    Centrifuged sludge: 23% dryness
      Ressources recovery: Composting
Notes: Depending on the characteristics of the sludge, the recovery routes will be different

## Slide 11: Sludge treatment SAV
4 THERMAL CONDITIONING
Dried sludge
3 THICKENING
5 DEWATERING
2 DIGESTION
6 TREATMENT OF EFFLUENT FROM SLUDGE TREATMENT
Biogas
Back to the inlet of the WWTP
1 THICKENING

## Slide 12: Sludge treatment SEC
FURNACE
HEAT RECOVERY
ELECTROSTATIC FILTER
WET SCRUBBING
BAG FILTER
CATALYTIC TREATMENT
CHIMNEY
PRIMARY SLUDGE
BIOLOGICAL FILTERS
PHYSICO-CHEMICAL TREATMENT
BIOLOGICAL SLUDGE
2 DEWATERING
1 THICKENING
3 INCINERATION

## Slide 13: Sludge treatment SEG
2 DIGESTION
1 THICKENING
3 DEWATERING
4 DRYING

## Slide 14: Sludge valorization paths (2017)
61% recycled to land
Notes: Ashes : 8 035 t
FGCR : 770 t
Here is the distribution of the different sectors of ressources recovery of our sludge. To date, agricultural valorization represents the largest share with more than 60% of valorization in

## Slide 15: SLUDGE Foccus on agricultural valorization

## Slide 16: Characteristics of Seine Aval’s sludge
On average 50.54% dry matter
 Solid and stabilized sludge (heap storage possible)
Result of a heat treatment pushed
 Hygienised sludge
Rich in Phosphorus and Sulfur
 Fertilizer interest for crops
Rich in Calcium and Organic Matter
 Amending interest for soils
Other parameters | Weighted average
Dry Matter | 51,7
C/N | 12,69
pH | 8,39
Elements | Contents (en kg/t MB) | Availability factor | Quantities brought (en kg/ha) |  | Quantities available the 1st year (en kg/ha) | 
 |  |  | à 6 t/ha | à 8 t/ha | à 6 t/ha | à 8 t/ha
Total Nitrogen (TKN) % organic matter % Ammonia | 10,0 | - 7 % 100 % | 60,0 | 80,0 | 14 | 19
Magnesium (MgO) | 8,2 | 48 % | 49,2 | 65,6 | 3 | 5
Potassium (K2O) | 1,8 | 10 % | 10,8 | 14,4 | 11 | 14
Phosphore (P2O5) Lots standards | 5,2 | 75 % | 31,2 | 41,6 | 15 | 20
Lots > 55 kg/tMB (6t/ha)* | 0,7 | 75 % | 4,2 | 5,6 | 1 | 1
Soufre (SO3) | 48,3 | 44 % | 289,8 | 386,4 | 217 | 290
Availability factor | Contents (en kg/t) | Stability Index of Organic Matter | Quantities brought (en kg/ha) |  |  | Quantity of stable organic matter generated(en kg/ha) | 
 |  |  | à 6 t/ha |  | à 8 t/ha | à 6 t/ha | à 8 t/ha
Organic matter | 206,1 | 81 % | 1 236,6 | 1 648,8 |  | 1 002 kg | 1 336 kg
Calcium (CaO) | 61,8 | - | 370,8 | 494,4 |  | - | -
* For lots with a P2O5 content exceeding 55 kg / tMB, the application rate is reduced to around 6 t / ha in order to limit phosphorus inputs.
Notes: Only sludge from the Wastewater treatment plan of Seine aval can be spread in agriculture. They are the only ones to be the subject of a plan of spreading.
Cooking at 195 ° C (one hundred and ninety five) and 20 bar pressure for 45 minutes
In order to be spread under these conditions (storage at the end of the fields, continuous evacuation ...), the sludge must meet certain characteristics:

## Slide 17
Elements | Units | Spreaded sludge in 2017 |  |  | Produced sludge in 2017 |  |  | Regulatory limit values
Number of analyzes |  | 53 |  |  | 52 |  |  | 
Number of lots |  | 51 |  |  | 50 |  |  | 
 |  | Min. | Max. | Moy. | Min. | Max. | Moy. | 
Cd | mg/kg de MS | 1,6 | 5,5 | 3,0 | 1,3 | 4,5 | 2,5 | 10
Cr | mg/kg de MS | 45,0 | 79,5 | 61,1 | 45,0 | 67,0 | 58,9 | 1000
Cu | mg/kg de MS | 535,7 | 833,1 | 706,3 | 535,7 | 782,4 | 663,3 | 1000
Hg | mg/kg de MS | 1,4 | 2,9 | 1,9 | 1,4 | 3,0 | 1,8 | 10
Ni | mg/kg de MS | 20,9 | 34,6 | 26,8 | 20 9 | 45,3 | 29,4 | 200
Pb | mg/kg de MS | 91,0 | 195,0 | 127,7 | 91,0 | 168,0 | 132,3 | 800
Zn | mg/kg de MS | 1 443,0 | 2 059,3 | 1 724,8 | 1 443,0 | 2 059,3 | 1657,2 | 3 000
Cr+Cu+Ni+Zn | mg/kg de MS | 2051,0 | 2921,0 | 2519,0 | 2 051,0 | 2 843,0 | 2408,8 | 4 000
Elements | Units | Spreaded sludge in 2017 |  |  | Produced sludge in 2017 |  |  | Regulatory limit values
Number of analyzes |  | 53 |  |  | 52 |  |  | 
Number of lots |  | 51 |  |  | 50 |  |  | 
 |  | Min. | Max. | Moy. | Min. | Max. | Moy. | 
Somme 7 PCB | mg/kg de MS | 0,07 | 0,34 | 0,20 | 0,08 | 0,27 | 0,18 | 0,8
Fluoranthène | mg/kg de MS | 0,39 | 1,00 | 0,60 | 0,46 | 1,00 | 0,77 | 5,0
Benzo(b)fluoranthène | mg/kg de MS | 0,11 | 0,47 | 0,20 | 0,11 | 0,50 | 0,32 | 2,5
Benzo(a)pyrène | mg/kg de MS | 0,10 | 0,41 | 0,20 | 0,10 | 0,48 | 0,27 | 2,0
Content in organic trace compounds sludge of Seine aval
The averages expressed are weighted by the tonnage of each lot.
Metallic Trace Element content of Seine aval sludge
The averages expressed are weighted by the tonnage of each lot.
Characteristics of Seine Aval’s sludge
Notes: We are subject to compliance with the limit values ​​of the regulations resulting from the decree of 8 January 1998 (one thousand nine hundred and ninety eight)

## Slide 18: Sludge spread perimeter
13 departments
1007 authorized municipalities
529 agricultural exploitations
163 347 total acres
155 214 acres spreadable

## Slide 19: Analytical monitoring of sludge and traceability
Sampling | Storage | Analysis
Weekly collection of 260 elementary samples as production progresses Constitution of a representative weekly average sample | Analysis of the average sample by a COFRAC accredited laboratory In situ sludge storage awaiting analysis results | Confirmation of conformity of the lot of sludge concerned Choice of the recovery or adapted disposal route
1 week of production = 1 VA - ETM - CTO analysis, 52 analyzes per year
1 batch = 1 to 2 weeks of production
Each lot of Seine aval sludge is therefore characterized by at least one complete analysis.
Notes: During a production week, with each mud pressed a sample is taken and will be a sample representation of the week.
The sludge is stored in well-defined storage cells until the return of the analyzes. No lot of mud is evacuated from the site without having the return of the analyzes.
The conformity of the sludge will make it possible to evacuate them in agricultural valorization (spreading or composting). If the sludge does not comply, it is sent to a non-hazardous waste landfill.

## Slide 20: Sludge treatment and valorization paths
 |  | Treatment stage and valorization path | WWTP
On-site treatment | Step 1 | Digestion | SAV, SAM, SEG
 | Step 2 | Dewatering | SAV, SAM, SEC, SEG, MAV, SEM
 |  | Drying | SAM, SEG
 |  | Thermal conditioning | SAV
On-site valorization | Step 3 | Incineration | SAM, SEC, MAV
Off-site valorization |  | Recycling to land | SAV
 |  | Compost | SAV, SAM, SEC, SEG, MAV, SEM
 |  | Off-site digestion | SAM, SEG
 |  | Cement plant | SAM, SEG

## Slide 21: SLUDGE Foccus on resources recovery

## Slide 22: Incineration residues
Ashes (9 000 t/year):
    Environmental characterization
     Recognized as non dangerous waste
    Valorization paths
     Landfill rehabilitation (at present)
    Extraction of phosphorus (future)
    Building materials (under study)
Flue gas cleaning residues (1 000 t/year):
  Regeneration
   Brine & gypsum
  … otherwise : Landfill
Notes: Bicarbonate de sodium : 2 NaHCO3 + SO2 + ½ O2 Na2SO4 + H20 + 2CO2
Ajout de CaCl + H20  NaCl CaSO4
On other treatment plants, we incinerate the sludge, which leads to the production of

## Slide 23: BIOGAS Energy recovery prospects

## Slide 24: BioGNVAL project
Integrated biogas upgrading and liquefaction technology
Demonstrator siting on the « Seine Amont » WWTP at Valenton
Flow(in) : 120 Nm3/hour of biogas
Production : 1 ton/day of bioLNG
: 1,5 ton/day of bioCO2
  BioLNG : Bio Liquid Natural Gas
1 000 Nm3
of Biogas
1 m3
of BioLNG
Notes:   Test objectives
    Prove the economic relevance of bioLNG (liquefied natural gas) production
    Check the cryogenic technology performance
    as biogas upgrading solution,
    Check the bioLNG (liquefied natural gas) compliance with vehicle fuel
    standards and industrial uses…
    Check the relevance of bioCO2 as cooling ,
    greenhouse,… uses.

## Slide 25: BioLNG and BioCO2 valorization
Notes: Here are the different types of possible bioLNG (liquefied natural gas) and carbon dioxide resources recovery as well as the different sources of biogas production
In France, since 2011, biogas can be injected in the natural gas network, after a specifical treatment.
Wastewater Treatment Plant will be the bioenergy factory of the future

## Slide 26: Biogas valorization paths
Biogas
« Light » treatment
Cogeneration
(Heat + Electricity))
Purification : Biomethane
Heat
Industry
Bio – NGV
200 bars
Compression
Odorization
Control
Gas network
4 to 16 bars
Liquefaction
BioLNG
- 160°C
Pipes
Heat network
Plant
needs
Electricity
Network
Site of production
Existing
Demonstrator
Under study
Notes: Natural gas for vehicle
In France, since 2011, biogas can be injected in the natural gas network, after a specifical treatment.
WWTP will be the bioenergy factory of the future

## Slide 27: BioLNG : Energetic Density Value
Transport and Storage volume reduction
1 000 Nm3
of Biogas
1 m3
of BioLNG
0,6 m3
of Diesel
The energy density is close to the diesel’s
Volumes divided by 1 000
Notes: 27

## Slide 28: BioLNG analysis
 | Units | Biogas | BioLNG | NGV standard
CH4 | % vol. | 61 | 98,6 | 83 min.
CO2 | % vol. | 38,7 | 0,45 | 14 max.
O2 | ppm v/v | 261 | 150 | N/A
N2 | % vol. | 0,33 | 0,95 | 14 max.
H2 | ppm v/v | 79 | 148 | 5 000 max.
H2S | ppm v/v | 5,5 | <DL | 10 max
Volatile organic residue | mg/Nm3 | 4,8 | <DL | N/A
Siloxanes | µg/Nm3 | 7 035 | 494 | 5 000 max.
Water | mg/Nm3 | N/A | <DL | 55 max.
NMHC | % vol. | N/A | <DL | 13 max.
Methane number | Kubesh | N/A | 100 | 70 min.
Standards for vehicle fuel

## Slide 29: Seine aval treatment plant actual energy balance
Process
Biogas
Purchased
Energy
145 GWh
7500 tCO2e
105 GWh
25 000 tCO2e
Heat
90 GWh
4500 tCO2e
Electricity
Gas turbine
313 GWh
Heat
60 GWh
14500 tCO2
42 000 tCO2e
Reduced emission
7500 tCO2e
Direct emission
Green Energy
Non Renewable Energy
Energy Self-sufficence : 69 %
Notes: Currently, we use the energy produced by sludge in the form of biogas to supply our customers with energy from the site in direct form with gas, but also electricity through gas turbines.
Thus, it allows us to reduce our carbon dioxide emissions.

## Slide 30: Seine aval treatment plant future energy balance
Green Energy
Non Renewable Energy
Process
Biogas
Purchased
Energy
274 GWh
14 000 tCO2e
105 GWh
25 000 tCO2e
Heat – Sludge incineration
345 GWh
Public Gas Grid
92 000 tCO2e
Avoided emission
42 000 tCO2e
Reduced emission
14 000 tCO2e
Direct emission
Heat
60 GWh
14500 tCO2
Energy Self-sufficence : 38 %
Notes: The desired evolution would be to increase the production of Biogas and to reinject it into the network.
At first the direct production of carbon dioxide would increase, but ultimately reduce overall.

## Slide 31: Heat recovery projects
Clichy : Wastewater networks waste heat recovery
63 000 MWh/year
10 000 housings
Start-up
on 2022
Clichy Plant
Wastewater field
Primary circuit
Plated heat exchanger
Heat pump
Secondary circuit
Heating network
Notes: At our Clichy site, we have a project for heat recovery at the effluent level. This would supply energy to a district heating network

## Slide 32
Marne Aval : Incinerator networks waste heat recovery
Neuilly sur Marne heat network
Partner : IDEX SGRM
Potential : 5 500 MWh/y
Heat recovery projects
Notes: On our MAV station, we have a project of study of heat recovery at the level of the incineration network

## Slide 33: SLUDGE Resources recovery prospects
Notes: The Seine river : a key feature of Paris landscape
And the SIAAP is in charche to protect and improve its quality

## Slide 34: Co-digestion project
Sewage sludge
Organic fraction from household waste
Digestate
Biogas
Digestate
Land
Energy
Co-digestion
Dedicated digestion
Energy
355 kg/y
75 kg/y
50 kg/y
500 kg/y
Innovation Partnership for combined digestion of organic maters
Notes: With the agency which is in charge of waste treatment in the parisian region, the SYCTOM, the objective is to produce more biogas from all organic fields

## Slide 35: Other innovative projects
Carbon sink : CO2 capture in incineration flue gas with microalgae : Demonstrator siting on the « Seine centre » WWTP
Integrated biogas upgrading and liquefaction technology : Demonstrator siting on the « Seine Amont » WWTP
Flow(in) : 120 Nm3/hour of biogas => Production : 1 ton/day of bioLNG + 1,5 ton/day of bioCO2
  BioLNG : Bio Liquid Natural Gas
1 000 Nm3
of Biogas
1 m3
of BioLNG
Other innovative projects
Notes: We are also working on two other projects:

## Slide 36: Thanks for your attention